## Storage Techs
Storage Technologies
Sources: | Hunter, C. A.; Penev, M. M.; Reznicek, E. P.; Eichman, J.; Rustagi, N.; Baldwin, S. F. Techno-Economic Analysis of Long-Duration Energy Storage and Flexible Power Generation Technologies to Support High-Variable Renewable Energy Grids. Joule 2021, 5 (8), 2077–2101. https://doi.org/10.1016/j.joule.2021.06.018. | [18 empty] | Data: |  | https://www.nrel.gov/storage/storefast.html
| Mongird, K.; Viswanathan, V.; Alam, J.; Vartanian, C.; Sprenkle, V.; Baxter, R. 2020 Grid Energy Storage Technology Cost and Performance Assessment. 2020, 12. | [20 empty] | https://www.pnnl.gov/thermal
| MIT Study on the Future of Energy Storage. 2022. | [20 empty] | https://energy.mit.edu/research/future-of-energy-storage/
Green cells indicate those that should align exactly with the values used in SEM / MEM
All Costs in $2019 USD |  | $2018 USD to $2019 USD | 1.02 |  | $2020 USD to $2019 USD | 0.9901
Electric Power System
Discount Rate | 0.07
Hours per year | 8760
Source: | Hunter et al. 2021 | [16 empty] | Mongird et al. 2020 |  | MIT 2022, page 177, Table 6.3
Technology | Li-ion |  | RFB |  | D-CAES ¦ Salt |  |  | A-CAES ¦Salt |  |  | PHS |  | P-TES |  | Stat-PEM ¦ Salt or PGP |  |  | Gravitational |  | Metal-air
Description | Li-ion battery. Source separates energy and power components, but we assume a 4 h duration with non-separated energy and power |  | Vanadium redox flow battery |  | Diabatic compressed air energy storage in which air is compressed into a salt dome cavern. Power is generated by using compressed air in a natural gas burner before feeding into a turbine which drives a synchronous generator |  |  | Adiabatic compressed air energy storage in which air is compressed into a salt dome cavern. Heat of compression is stored in thermal energy storage. Power is generated by reheating air with stored thermal energy and spinning a turbine to drive a synchronous generator |  |  | Closed loop pumped hydro storage using upper and lower water reservoirs |  | Pumped thermal energy storage |  | Hydrogen production via PEM electrolysis, power generation via a stationary PEM fuel cell, and hydrogen storage in a salt cavern |  |  | Gravitational energy storage. Mid value of capital costs and O&M costs separated by energy and power through linear regerssion (see corersponding spreadsheet) |  | Metal-air batteries, mid value from source taken
| Energy | Power | Energy | Power | Power In | Energy | Power Out | Power In | Energy | Power Out | Energy | Power | Energy | Power | Power In | Energy | Power Out | Energy | Power | Energy | Power
Total overnight cost ($/kWh for energy components and $/kW for power components) | 326.4 | 250.92 | 199.92 | 1411.68 | 517.14 | 17.85 | 774.18 | 517.14 | 51.102 | 774.18 | 105.162 | 1644.24 | 37.842 | 1703.4 | 1706.46 | 1.9992 | 1414.74 | 116.6334 | 1415.9139 | 2.448 | 655.86
Fixed O&M (% of capital cost or $/kWh/yr $/kW/yr) | 4.24% | 8.466 | 1.5% | 8.4252 | 13.8108 | 1.5% | 13.8108 | 13.8108 | 1.5% | 13.8108 | 1.5% | 12.75 | 1.5% | 13.872 | 13.056 | 1.5% | 13.056 | 0.57623 | 11.8329 | 0.102 | 16.422
Fixed property tax, insurance, licensing, permiting (% of capital cost) | - | 1.5% | - | 1.5% | 1.5% | - | 1.5% | 1.5% | - | 1.5% | - | 1.5% | - | 1.5% | 1.5% | - | 1.5% | - | - | - | -
Assumed Lifetime (yr) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 49 | 49 | 30 | 30
Capital recovery factor (%/yr) | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 7.264% | 7.264% | 8.059% | 8.059%
Fixed Annual Costs ($/kWh/yr, $/kW/yr) | 27.4187 | 28.9901 | 16.3525 | 123.8938 | 56.1104 | 1.46 | 77.135 | 56.1104 | 4.1799 | 77.135 | 8.6017 | 147.2409 | 3.0953 | 153.2019 | 152.6362 | 0.16352 | 128.7749 | 9.0483 | 114.6828 | 0.29928 | 69.2754
Fixed Hourly Costs ($/kWh/h, $/kW/h) | 0.00313 | 0.0033094 | 0.0018667 | 0.014143 | 0.0064053 | 0.00016667 | 0.0088054 | 0.0064053 | 0.00047716 | 0.0088054 | 0.00098193 | 0.016808 | 0.00035334 | 0.017489 | 0.017424 | 1.8667e-05 | 0.0147 | 0.0010329 | 0.013092 | 3.4164e-05 | 0.0079082
Total Fixed Hourly Costs for Li-ion ($/kWh) | 0.0039573
Variable O&M ($/MWh) | - | 0.0031 | - | 0.02689 | 0 | - | 0.0033 | 0 | - | 0.0033 | - | 0.0003 | - | 0.0033 | 0.0013 | - | 0.0028 | - | 0.5125 | - | 0
Variable Cost ($/kWh) | - | 3.1e-06 | - | 2.689e-05 | 0 | - | 3.3e-06 | 0 | - | 3.3e-06 | - | 3e-07 | - | 3.3e-06 | 1.3e-06 | - | 2.8e-06 | - | 0.0005125 | - | 0
Decay rate (% per hour) | - | - | - | - | - | - | - | - | - | - | - | - | 0.000625 | - | - | 4.1667e-05 | - | - | - | - | -
Efficiency (%) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 50% | - | 71% | - | - | - | 73% up, 63% down
Round-Trip Efficiency (%) | 86% |  | 75% |  | 55% |  |  | 65% |  |  | 81% |  | 52% |  | 36% |  |  | 84% |  | 46%
Note
Note on U21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumed, not provided
Note on V21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumed, not provided

## Gravitational
Source: | https://www.pnnl.gov/gravitational
Data: | Gravitational Costs & Performance Parameters (obtained 7-18-2022)
We use the 1000 MW plant as the reference plant, and estimate energy and power capacity costs using linear regression
Equations we assume:
| Low |  | Midpoint |  | High
E/P Ratio (h) | Total ESS Installed Cost ($/kW) | Total Fixed O&M Cost ($/kW-yr) | Total ESS Installed Cost ($/kW) | Total Fixed O&M Cost ($/kW-yr) | Total ESS Installed Cost ($/kW) | Total Fixed O&M Cost ($/kW-yr)
2 | 922 | 8.15 | 1326 | 13.12 | 1863 | 15.6
4 | 1341 | 11.64 | 1706 | 14.28 | 2253 | 15.6
6 | 1726 | 15.13 | 2045 | 15.44 | 2583 | 15.6
8 | 1972 | 15.6 | 2362 | 16.61 | 2879 | 18.62
10 | 2185 | 15.6 | 2664 | 17.77 | 3236 | 22.12
24 | 3318 | 15.6 | 4564 | 25.92 | 6137 | 46.56
100 | 6776 | 15.6 | 13145 | 70.15 | 22060 | 179.26
| Energy Capacity | Power Capacity | Energy Capacity | Power Capacity | Energy Capacity | Power Capacity
Total Installed Cost ($/kWh, $/kW) | 53.5712 | 1529.1971 | 117.7998 | 1430.073 | 207.6605 | 1263.9343
Fixed O&M ($/kWh/yr, $/kW/yr) | 0.01348 | 14.5202 | 0.58199 | 11.9513 | 1.7326 | 5.7349
𝑇𝑜𝑡𝑎𝑙 𝐸𝑆𝑆 𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑜𝑠𝑡 ($/𝑘𝑊)=𝑇𝑜𝑡𝑎𝑙 𝑃𝑜𝑤𝑒𝑟 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐶𝑜𝑠𝑡 ($/𝑘𝑊)+𝐸𝑛𝑒𝑟𝑔𝑦 𝑡𝑜 𝑃𝑜𝑤𝑒𝑟 𝑅𝑎𝑡𝑖𝑜 (ℎ)×𝑇𝑜𝑡𝑎𝑙 𝐸𝑛𝑒𝑟𝑔𝑦 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐶𝑜𝑠𝑡 ($/𝑘𝑊ℎ)
𝑇𝑜𝑡𝑎𝑙 𝐹𝑖𝑥𝑒𝑑 𝑂&𝑀 𝐶𝑜𝑠𝑡 ($/(𝑘𝑊⋅𝑦𝑟))=𝑃𝑜𝑤𝑒𝑟 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐹𝑖𝑥𝑒𝑑 𝑂&𝑀 𝐶𝑜𝑠𝑡 ($/(𝑘𝑊⋅𝑦𝑟))+𝐸𝑛𝑒𝑟𝑔𝑦 𝑡𝑜 𝑃𝑜𝑤𝑒𝑟 𝑅𝑎𝑡𝑖𝑜 (ℎ)×𝐸𝑛𝑒𝑟𝑔𝑦 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝐹𝑖𝑥𝑒𝑑 𝑂&𝑀 𝐶𝑜𝑠𝑡 ($/(𝑘𝑊ℎ⋅𝑦𝑟))

## Generation Techs
NREL ATB 2019 Case Scenario
Source: | NREL (National Renewable Energy Laboratory). 2021. "2021 Annual Technology Baseline." Golden, CO: National Renewable Energy Laboratory. https://atb.nrel.gov/.
Data: | https://atb.nrel.gov/electricity/2022/data
Green cells indicate those that should align exactly with the values used in SEM / MEM
Cost values used in Dave and Tyler's version
Cost values newly added
MWh/MMBtu | 0.29307 | https://www.eia.gov/totalenergy/data/monthly/pdf/sec13_18.pdf
Electric Power System
Discount Rate | 0.07 |  | NREL units
Hours per year | 8760 |  | lbs/MMBtu | lbs/Btu | lbs/kWh | kg/kWh
Btu / kWh | 3412.1416 |  | 118.6248 | 0.00011862 | 0.40476 | 0.1836
Costs for new nuclear sectors are in 2017 $, and other costs are in 2019 $ | Solar - Utility PV 2019 | Land-based Wind 2019 | Nuclear 2019 | Utility-Scale 4Hr Battery Storage Advanced | Gas-CC Advanced | Gas-CC-CCS Advanced | Biopower | Geothermal EGS Flash Advanced | Offshore Wind Class 8 Advanced | Offshore Wind Class 8 Moderate | Offshore Wind Class 8 Conservative | Offshore Wind Class 1 Advanced | Offshore Wind Class 1 Moderate | Offshore Wind Class 1 Conservative
Total overnight cost ($/kW for generator or $/kWh for storage) | 1391 | 1436 | 7388 | 290 | 1054 | 2670 | 4346 | 19977 | 5002 | 5183 | 5469 | 3534 | 3668 | 3885
Fixed O&M ($/kW-yr) | 23 | 43 | 145 | 36 | 27 | 65 | 150 | 268 | 80 | 83 | 88 | 110 | 114 | 121
Assumed Lifetime | 30 | 30 | 30 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Capital recovery factor (% per year) | 8.059% | 8.059% | 8.059% | 10.98% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059% | 8.059%
ACC | 135.0957 | 158.7221 | 740.3723 | 67.8404 | 111.9381 | 280.1657 | 500.2285 | 1877.8746 | 483.0932 | 500.6793 | 528.727 | 394.7924 | 409.5909 | 434.0782
FHC | 0.015422 | 0.018119 | 0.084517 | 0.0077443 | 0.012778 | 0.031982 | 0.057104 | 0.21437 | 0.055148 | 0.057155 | 0.060357 | 0.045068 | 0.046757 | 0.049552
Variable O&M ($/MWh) |  |  | 2 |  | 2 | 6 | 5
Heat Rate (Btu/kWh) |  |  | 10460 |  | 6360 | 5180 | 13500
Efficiency |  |  | 0.32621 |  | 0.5365 | 0.65871 | 0.25275
Fuel Cost ($/MWh) |  |  | 7 |  | 8 | 8 | 43
Variable Cost ($/MWh) |  |  | 9 |  | 10 | 14 | 48
Decay rate (% per hour)
Round-Trip Efficiency |  |  |  | 0.85
Total cost for nuclear |  |  | 9.0845
Note